SHORT COURSE SYLLABUS

PLC PROGRAMMING & INTEGRATION

Allen-Bradley (Rockwell Automation) — CompactLogix / ControlLogix

| DURATION 8 Hours | MODULES 8 | HARDWARE Allen-Bradley PLC | LEVEL Beginner to Intermediate |
| --- | --- | --- | --- |

| Institution |  |
| --- | --- |
| Instructor | Prof. Dr. Syed Ahmed |
| Course Code |  |
| Academic Term | 2026 |

# Course Overview

This intensive 8-hour course provides a structured, hands-on introduction to Programmable Logic Controller (PLC) programming and system integration using the Allen-Bradley (Rockwell Automation) platform. Participants progress from fundamental PLC concepts through to practical HMI integration, industrial communication protocols, and professional programming practices. Every module combines instructor-led theory with live demonstrations and laboratory exercises on real or emulated CompactLogix hardware.

| Course Title | PLC Programming & Integration (Allen-Bradley) |
| --- | --- |
| Duration | 8 Hours (1 intensive day or 2 × 4-hour sessions) |
| Level | Beginner to Intermediate — Industrial Automation |
| Format | Instructor-led lectures, live demonstrations, and hands-on lab exercises |
| Prerequisites | Basic electrical knowledge; no prior PLC programming experience required |
| Hardware | Allen-Bradley CompactLogix or MicroLogix PLC (physical or emulated via RSLogix 500/5000) |
| Software | Studio 5000 Logix Designer (or RSLogix 5000), RSLinx Classic, Factory Talk View SE/ME |
| Certification | Certificate of Completion issued upon finishing all modules and passing the final quiz |

# Learning Outcomes

Upon successful completion of this course, participants will be able to:

- Describe the Allen-Bradley PLC hardware architecture and select appropriate hardware for a given application

- Create and configure a Studio 5000 Logix Designer project including tag database and I/O tree

- Write fully functional Ladder Logic programs using contacts, coils, timers, counters, and arithmetic instructions

- Configure digital and analog I/O modules and correctly apply sinking/sourcing wiring concepts

- Set up EtherNet/IP communication and MSG instructions for controller-to-controller data exchange

- Design and deploy HMI screens using Factory Talk View ME with live PLC tag binding

- Use Studio 5000 diagnostic tools to identify, interpret, and clear controller faults

- Apply professional PLC programming standards: naming conventions, AOIs, modular code structure, and FAT procedures

# Schedule at a Glance

All times are indicative and may be adjusted by the instructor. Labs are integrated within each module time block.

| Mod. | Time | Module Title | Duration | Format | Lab? |
| --- | --- | --- | --- | --- | --- |
| 1 | 08:00 | Introduction to PLCs & Allen-Bradley Ecosystem | 45 min | Lecture | No |
| 2 | 08:45 | Studio 5000 Environment & Project Setup | 60 min | Demo + Lab | Yes |
| 3 | 09:45 | Ladder Logic Programming — Fundamentals | 75 min | Demo + Lab | Yes |
| — | 11:00 | BREAK | 15 min | — | — |
| 4 | 11:15 | Timers, Counters & Data Handling Instructions | 60 min | Demo + Lab | Yes |
| 5 | 12:15 | I/O Configuration & Wiring (Digital, Analog & Safety) | 45 min | Demo | No |
| — | 13:00 | LUNCH BREAK | 45 min | — | — |
| 6 | 13:45 | Communication Protocols — EtherNet/IP & DeviceNet | 60 min | Demo + Lab | Yes |
| 7 | 14:45 | HMI Integration with Factory Talk View | 60 min | Demo + Lab | Yes |
| — | 15:45 | BREAK | 15 min | — | — |
| 8 | 16:00 | Fault Diagnostics, Safety & Best Practices | 60 min | Lecture+Lab | Yes |
| — | 17:00 | Final Quiz & Wrap-Up Q&A | 30 min | Assessment | — |
| TOTAL COURSE TIME |  | 8 Hours Instruction + 60 min Breaks = ~9.5 Hours Total |  |  |  |  |

# Detailed Module Breakdown

| MOD 1 | Introduction to PLCs & the Allen-Bradley Ecosystem | ⏱ 45 Minutes |
| --- | --- | --- |
| Learning Objectives | ▸ Explain what a PLC is and how it differs from a relay-based control system ▸ Identify the key hardware components of an Allen-Bradley CompactLogix/ControlLogix system ▸ Describe the Allen-Bradley product family and select the correct PLC for a given application ▸ Understand the PLC scan cycle (Input Scan → Program Execution → Output Scan → Housekeeping) ▸ Recognise key IEC 61131-3 programming languages supported by Studio 5000 |
| Topics Covered | ▸ History of PLCs: from relay panels to modern networked controllers ▸ Allen-Bradley product families: MicroLogix, CompactLogix, ControlLogix, GuardLogix ▸ PLC hardware anatomy: CPU, I/O modules, power supply, chassis, backplane ▸ Discrete vs Analog I/O — voltage levels, current sinking vs sourcing ▸ The PLC scan cycle in detail — timing, priority, and common misconceptions ▸ IEC 61131-3 programming languages: LD, FBD, ST, SFC, IL — when to use each ▸ Introduction to Studio 5000 Logix Designer software interface ▸ Course overview, safety rules in the lab, and expectations |
| Lab Exercise | No hands-on lab for this module. Instructor demonstrates the CompactLogix hardware and walks through the Studio 5000 interface. Students identify physical components on the trainer unit. |
| Software Used | Studio 5000 Logix Designer (read-only tour), RSLinx Classic (overview) |

| MOD 2 | Studio 5000 Environment & Project Setup | ⏱ 60 Minutes |
| --- | --- | --- |
| Learning Objectives | ▸ Create a new Studio 5000 project and configure the correct controller type and firmware revision ▸ Build a tag database using controller-scoped and program-scoped tags ▸ Select appropriate data types (BOOL, INT, DINT, REAL, STRING, UDT) for different variables ▸ Configure Ethernet properties and establish a communication path using RSLinx ▸ Download a project to the CompactLogix PLC and switch between Program/Run/Remote modes ▸ Use online monitoring to watch tag values change in real time |
| Topics Covered | ▸ Creating a new project: controller type, chassis, slots, firmware revision ▸ Project organiser pane: Controller, Tasks, Programs, Add-On Instructions, Data Types, I/O Configuration ▸ Tag database fundamentals: tag name conventions, data types, aliases, and descriptions ▸ User-Defined Data Types (UDTs) — structuring complex data for motors, valves, and sensors ▸ RSLinx Classic: driver configuration (EtherNet/IP, USB, Serial), Who Active browser ▸ Download / Upload procedure — going Online vs Offline, Flash updates ▸ Controller modes: Program, Run, Remote Program, Remote Run — when each is used ▸ Online monitoring: Watch window, tag monitor, forced I/O overview |
| Lab Exercise | Lab 2-A: Create a new CompactLogix project from scratch. Configure the I/O tree for 16 DI + 16 DO digital modules. Create a UDT for a 3-phase motor (running, faulted, speed_rpm, start_cmd). Download to the emulator or physical PLC. Verify tags in the online monitor. |
| Software Used | Studio 5000 Logix Designer, RSLinx Classic, Emulate 5000 |

| MOD 3 | Ladder Logic Programming — Fundamentals | ⏱ 75 Minutes |
| --- | --- | --- |
| Learning Objectives | ▸ Write Ladder Logic rungs using XIC, XIO, OTE, OTL, OTU instructions correctly ▸ Implement Examine If Closed (XIC) and Examine If Open (XIO) contacts for digital input logic ▸ Use output coil (OTE), latch (OTL), and unlatch (OTU) instructions for output control ▸ Build a fully functional Start-Stop-Seal circuit with Normally Open start and Normally Closed stop ▸ Apply comparison instructions (EQU, NEQ, LES, GRT, LEQ, GEQ) for numeric logic ▸ Perform arithmetic operations (ADD, SUB, MUL, DIV, MOD, SQR) in Ladder Logic ▸ Implement branching (parallel rungs) and nested logic structures |
| Topics Covered | ▸ Ladder Logic fundamentals: rungs, power rail, contacts, and coils ▸ XIC (Examine If Closed) — energised when tag bit = 1 ▸ XIO (Examine If Open) — energised when tag bit = 0 ▸ OTE (Output Energise), OTL (Latch), OTU (Unlatch) — differences and correct use cases ▸ Classic motor starter: Start-Stop-Seal circuit construction and fault behaviour ▸ Comparison instructions: EQU, NEQ, LES, GRT, LEQ, GEQ — IN vs IN1 structure ▸ Arithmetic instructions: ADD, SUB, MUL, DIV, MOD — Source A, Source B, Destination ▸ SQR, ABS, CPT (Compute) — mathematical expressions in one instruction ▸ Move instruction (MOV, MVM): copying data between tags, bit masking ▸ Program branching: parallel rungs, OR logic, nested branches, best practices |
| Lab Exercise | Lab 3-A: Write a complete motor control program including: (1) Start/Stop/E-Stop with seal-in, (2) Run indicator light, (3) Fault reset logic, (4) Auto/Manual mode selector using XIC/XIO/OTE/OTL/OTU. Simulate using forced I/O. Lab 3-B: Write arithmetic rungs to calculate: pump flow rate (REAL arithmetic), unit conversion (°F to °C), and a running total counter using ADD. |
| Software Used | Studio 5000 Logix Designer, Emulate 5000, forced I/O simulation |

| MOD 4 | Timers, Counters & Data Handling Instructions | ⏱ 60 Minutes |
| --- | --- | --- |
| Learning Objectives | ▸ Configure and use TON (Timer On Delay), TOF (Timer Off Delay), and RTO (Retentive Timer On) instructions ▸ Implement CTU (Count Up), CTD (Count Down), and CTUD (Count Up/Down) counter instructions ▸ Use timer and counter status bits (.DN, .EN, .TT, .CU, .CD, .OV) in logic branching ▸ Apply sequencer instructions (SQO, SQL, SQI) for multi-step machine sequences ▸ Implement File Arithmetic Logic (FAL) and File Copy (COP) for array and block data operations ▸ Design a multi-step production sequence using timers and counters |
| Topics Covered | ▸ TON (Timer On Delay): Preset, Accumulated, .EN, .TT, .DN bits — wiring and timing diagram ▸ TOF (Timer Off Delay): inversion of on-delay — common use cases in cooling systems ▸ RTO (Retentive Timer): accumulated value retained when rung goes false — power loss considerations ▸ CTU / CTD / CTUD: counter bits .CU, .CD, .DN, .OV, .UN, .UC, .DC — reset coil (RES) ▸ Practical timer applications: alarm delays, dwell times, heartbeat/watchdog timers ▸ Practical counter applications: parts counting, batch totalling, cycle counting ▸ Sequencer Output (SQO): step-based output control — truth table approach ▸ FAL (File Arithmetic Logic): performing math on arrays — recipe scaling, PID setpoints ▸ COP / FLL (Copy File / Fill File): batch data copy, array initialisation ▸ Designing a 5-step conveyor sequence using TON, CTU, and sequencer logic |
| Lab Exercise | Lab 4-A: Build a traffic-light controller using three TON timers — Red (30s), Green (25s), Amber (5s) — cycling continuously with a pedestrian-request input. Lab 4-B: Implement a batch counter that counts 100 parts, stops the line, triggers an alarm, waits for operator reset, then restarts. Use CTU, TON (alarm delay), and OTL/OTU. |
| Software Used | Studio 5000 Logix Designer, Emulate 5000 |

| MOD 5 | I/O Configuration, Wiring & Safety Considerations | ⏱ 45 Minutes |
| --- | --- | --- |
| Learning Objectives | ▸ Configure digital and analog I/O modules in the Studio 5000 I/O tree correctly ▸ Understand sinking vs sourcing wiring for NPN and PNP field devices ▸ Configure analog input/output scaling (engineering units to raw counts) in Studio 5000 ▸ Connect and configure a 4–20 mA analog pressure transmitter in software ▸ Recognise safety I/O requirements and how GuardLogix differs from standard ControlLogix ▸ Apply proper I/O module fault handling and connection behaviour configuration |
| Topics Covered | ▸ Studio 5000 I/O tree: adding modules, selecting catalogue numbers, slot addressing ▸ Digital input module wiring: sinking (NPN) vs sourcing (PNP) — field device compatibility ▸ Digital output module wiring: relay, transistor (DC), and triac (AC) output types ▸ Analog I/O fundamentals: 0–10V, 4–20mA, ±10V — resolving 12-bit and 16-bit counts ▸ Configuring analog scaling in Studio 5000: Input Min/Max, Scaled Min/Max, Engineering Units ▸ I/O module fault handling: major vs minor faults, Hold Last State vs Reset to Zero ▸ Produced/Consumed tags overview — sharing real-time data between ControlLogix controllers ▸ Introduction to safety PLCs: GuardLogix, safety-rated I/O, E-Stop, Safety Mat, Light Curtain wiring ▸ Field device fundamentals: limit switches, proximity sensors, photoelectric sensors, VFDs, solenoids |
| Lab Exercise | No extended lab for this module. Instructor-led demonstration: connect a 4–20 mA simulated pressure transmitter to an analog input module, configure scaling in Studio 5000, and display the engineering unit value (0–100 PSI) on the HMI tag (covered in Module 7). |
| Software Used | Studio 5000 Logix Designer (I/O configuration), RSLinx (module diagnostics) |

| MOD 6 | Communication Protocols — EtherNet/IP, DeviceNet & Messaging | ⏱ 60 Minutes |
| --- | --- | --- |
| Learning Objectives | ▸ Explain the EtherNet/IP protocol stack, CIP (Common Industrial Protocol), and how it differs from standard Ethernet ▸ Configure an EtherNet/IP adapter module in Studio 5000 and verify live communication ▸ Use MSG (Message) instructions for explicit messaging between two CompactLogix controllers ▸ Describe DeviceNet, ControlNet, and DH-485 protocols and their typical application areas ▸ Configure produced and consumed tags to share data between controllers on EtherNet/IP ▸ Troubleshoot common Ethernet communication faults using RSLinx and module LED diagnostics |
| Topics Covered | ▸ Industrial Ethernet vs commercial Ethernet — determinism, prioritisation, cable selection ▸ CIP (Common Industrial Protocol): object model, explicit messaging, implicit messaging (I/O) ▸ EtherNet/IP addressing: IP configuration in Studio 5000, DHCP vs static addressing ▸ MSG instruction: Message type (CIP Generic, PLC5 Read/Write, SLC Read/Write), Connected vs Unconnected ▸ Produced & Consumed Tags: configuration, unicast vs multicast, real-time data sharing ▸ DeviceNet overview: network scanner, device node addressing, EDS files, commissioning ▸ ControlNet overview: deterministic scheduled messaging — media redundancy considerations ▸ DH+ / DH-485: legacy networks — bridging via 1785-KE/1784-KTX gateways ▸ Network topology design: star vs ring vs linear — redundancy and media considerations ▸ Fault diagnosis: MSP LED patterns, RSLinx diagnostics, event log, module status in Studio 5000 |
| Lab Exercise | Lab 6-A: Configure a MSG instruction to read 10 DINT tags from a second CompactLogix (or emulated controller). Trigger the read every 500ms using a TON. Display the received values in the Watch window. Lab 6-B: Configure produced/consumed tags between two controllers and verify real-time data synchronisation. |
| Software Used | Studio 5000 Logix Designer, RSLinx Classic (EtherNet/IP driver), Emulate 5000 (two instances) |

| MOD 7 | HMI Integration with Factory Talk View ME/SE | ⏱ 60 Minutes |
| --- | --- | --- |
| Learning Objectives | ▸ Create a new Factory Talk View ME project and configure the PLC communication shortcut ▸ Design HMI screens with pushbuttons, indicator lights, numeric displays, and trend charts ▸ Bind HMI objects to PLC tags using direct addressing and tag database import ▸ Configure alarm detection and display using Factory Talk View alarm objects ▸ Test HMI screens in Test Display mode and download to a PanelView terminal or PC Runtime ▸ Explain the difference between Factory Talk View ME (machine-level) and SE (supervisory-level) |
| Topics Covered | ▸ Factory Talk View ME vs SE: architecture differences, use cases, licensing ▸ Creating a new application: shortcut configuration, RSLinx Enterprise OPC server setup ▸ Display types: Standard, Global Object, Parameter File display — when to use each ▸ HMI object library: Pushbutton, Momentary PB, Maintained PB, Pilot Light, Numeric Display/Entry ▸ Tag addressing in HMI: {PLC_Shortcut}:Program:Tag_Name vs controller-scoped tags ▸ Graphic library: importing custom images, using Global Objects for reusable motor/valve symbols ▸ Alarm setup: Alarm Setup Wizard, HI/HIHI/LO/LOLO limit alarms, acknowledgement handling ▸ Trends: Real-time trend, Historical trend — data log model configuration ▸ Security: operator/engineer/administrator access levels, login screens ▸ Downloading to PanelView Plus / running on PC with ME Station runtime |
| Lab Exercise | Lab 7-A: Build a 3-screen HMI for the motor control program: (1) Main Control Screen with Start/Stop PBs and Run/Fault indicators, (2) Analog Status Screen showing pressure gauge and trend, (3) Alarm Summary Screen. Connect all objects to PLC tags and test in Test Display mode. |
| Software Used | Factory Talk View ME v10, RSLinx Enterprise, Studio 5000 (running program for live tag testing) |

| MOD 8 | Fault Diagnostics, Safety & PLC Programming Best Practices | ⏱ 60 Minutes |
| --- | --- | --- |
| Learning Objectives | ▸ Use the Studio 5000 diagnostic tools to identify and clear major and minor controller faults ▸ Read and interpret the controller fault log, I/O module status, and connection status ▸ Apply structured programming best practices: naming conventions, modular code, comment standards ▸ Implement a structured Add-On Instruction (AOI) for a reusable motor starter block ▸ Describe NFPA 79 and ISO 13849 requirements relevant to PLC-based safety systems ▸ Create a commissioning and FAT (Factory Acceptance Test) checklist for a PLC project |
| Topics Covered | ▸ Controller fault types: Major (halts execution) vs Minor (continues) — fault code table ▸ Reading the fault log: Studio 5000 Controller Properties → Fault Log tab ▸ I/O module fault diagnostics: red LED patterns, connection fault bits in I/O tree ▸ Cross-reference tool: find all rungs that use a specific tag — change management ▸ Add-On Instructions (AOIs): creating a Motor Starter AOI with In/Out/InOut parameters ▸ Programming standards: naming conventions (MOTOR_001_START_PB), commenting, task structure ▸ Program organisation: Periodic vs Event vs Continuous tasks — CPU load management ▸ NFPA 79 (Electrical Standard for Industrial Machinery) — relevant PLC safety clauses ▸ ISO 13849-1 / IEC 62061: safety integrity levels, PLr, SIL rating for safety functions ▸ FAT (Factory Acceptance Test) procedure: I/O loop check, alarm testing, interlock verification ▸ Change management and backup procedures: archive, compare, version control for PLC code |
| Lab Exercise | Lab 8-A: Create an AOI named 'MOT_STARTER' with parameters: Start_Cmd (BOOL In), Stop_Cmd (BOOL In), Fault_Reset (BOOL In), Running (BOOL Out), Faulted (BOOL Out). Instantiate the AOI for two motors in the main program. Lab 8-B: Deliberately introduce a major fault (remove I/O module in software), identify the fault code, clear it, and document the procedure. |
| Software Used | Studio 5000 Logix Designer (AOI editor, cross-reference, fault log), Emulate 5000 |

# Assessment & Grading

All assessments are designed to reinforce practical skills alongside theoretical knowledge. Participants must achieve a combined score of 70% or above to receive the Certificate of Completion.

| Assessment Component | Description | When | Weight |
| --- | --- | --- | --- |
| Lab Exercises (7 labs) | Completion-based practical tasks per module. Each graded on functionality and correctness. | During class | 35% |
| Module Check-ins (8 quizzes) | 5-question knowledge check at the end of each module — multiple choice and short answer. | End of each module | 25% |
| Mid-Course Project | Build a working Ladder Logic program for a conveyor belt start/stop/e-stop sequence with HMI. | After Module 4 | 20% |
| Final Assessment Quiz | 30-question written quiz covering all 8 modules. Open-book for reference material only. | End of day | 20% |

## Grading Scale

| Score Range | Grade | Description |
| --- | --- | --- |
| 90–100% | Distinction | Exceptional understanding and lab execution |
| 75–89% | Pass with Merit | Strong understanding with minor gaps |
| 70–74% | Pass | Meets minimum competency requirements |
| < 70% | Not Yet Competent | Recommend repeat attendance or further self-study |

# Tools, Software & Equipment

The following hardware and software are used throughout this course. Software licences for Studio 5000 and Factory Talk View are required per workstation. A 30-day trial version is available from Rockwell Automation for participants without a licence.

| Tool / Software | Version / Model | Purpose in This Course |
| --- | --- | --- |
| Studio 5000 Logix Designer | v32 or later | Primary programming environment — Ladder Logic, Function Block, Structured Text for ControlLogix / CompactLogix |
| RSLogix 500 | v12 or later | Programming tool for MicroLogix and SLC 500 series PLCs — covered in Module 1 overview |
| RSLinx Classic | v4.00+ | OPC server and communications gateway — connects PLC to PC, manages Ethernet and serial connections |
| Factory Talk View ME/SE | v10 or later | HMI development environment — tag binding, screen design, alarm management in Module 7 |
| Allen-Bradley CompactLogix 5370 | L1/L2/L3 series | Primary lab hardware — 24V DC digital I/O, 0-10V analog, EtherNet/IP port |
| Allen-Bradley MicroLogix 1100 | 1763-L16BWA | Alternative / backup lab PLC — simpler hardware, ideal for Modules 2 & 3 |
| Emulate 5000 | Included with Studio 5000 | Software PLC emulator — allows programming practice without physical hardware |
| EtherNet/IP Switch (unmanaged) | Any 1 Gbps switch | Connects PLC, HMI panel, and engineering workstation on the same network segment |

# Recommended References & Resources

The following materials are provided as reference during and after the course. Rockwell Automation publications referenced below are available as free PDF downloads from literature.rockwellautomation.com.

| Resource | Publisher / Source | Notes |
| --- | --- | --- |
| Logix 5000 Controllers General Instructions Reference Manual | Rockwell Automation (Publication 1756-RM003) | Comprehensive instruction set reference — provided as PDF handout. Essential for all modules. |
| Studio 5000 Logix Designer Getting Started Guide | Rockwell Automation (LGSE-QS001) | Step-by-step project creation, tag database setup, and download procedure. |
| CompactLogix System User Manual | Rockwell Automation (1769-UM021) | Hardware installation, I/O wiring diagrams, and specifications for lab PLC. |
| Programmable Controller Industrial Automation Pocket Guide | Siemens / IAONA (free download) | Vendor-neutral overview of PLC standards (IEC 61131-3) and architecture. |
| PLCopen IEC 61131-3 Standard | PLCopen Organisation | Programming language standards — Ladder, FBD, ST, SFC, IL. Referenced in Module 3. |
| Rockwell Automation TechConnect Support Portal | support.rockwellautomation.com | Firmware downloads, knowledgebase articles, and online documentation updates. |
| RA Online Course: Introduction to Logix5000 Controllers | Rockwell Automation University | Free supplementary e-learning — reinforces classroom content with interactive exercises. |

# Instructor Notes & Delivery Guidelines

- Labs should account for approximately 40% of total class time — do not skip or shorten lab exercises to recover time from lecture overruns.

- Ensure all participant workstations have Studio 5000 v32+ and RSLinx installed and licence-activated before the session begins. Test Emulate 5000 connectivity the day before.

- For participants without physical hardware, Emulate 5000 supports all labs in Modules 2–4 and 6–8. Modules 5 and 7 benefit significantly from physical I/O wiring — arrange a hardware demo station if possible.

- Module 3 (Ladder Logic Fundamentals) is the most technically dense — allocate 10 extra minutes from the break buffer if participants are struggling with OTL/OTU concepts.

- Encourage participants to save their projects after each lab. Provide a shared network drive or USB sticks for project backup.

- For participants with prior RSLogix 500 experience, highlight the key Studio 5000 differences in Module 2 to prevent confusion from legacy habits.

- The mid-course project (after Module 4) can be assigned as an individual or pair exercise — pairs recommended for classes of 12 or more participants.

— End of Syllabus Document —

PLC Programming & Integration (Allen-Bradley)  ·  8-Hour Short Course  ·  Industrial Automation Training